## Lines_corrected
from_bus | to_bus | length_km | cable_type | bundle_no | Dm | A | Rb | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | max_i_ka | cables | voltage | location
0 | 1 | 126 | Biggest | N/A | N/A | 500 | N/A | 0.053 | 0.11932 | 1.7e-09 | 0.545 | 1 | 132 | underwater
2 | 3 | 5.5997 | Merlin | 2 | 12 | 170.2 | 0.053543 | 0.1717 | 0.34006 | 1e-09 | 0.56 | 6 | 220 | overhead
3 | 4 | 15.0251 | Merlin | 2 | 12 | 170.2 | 0.053543 | 0.1717 | 0.34006 | 1e-09 | 0.56 | 3 | 220 | overhead
3 | 4 | 14.8977 | Merlin | 2 | 12 | 170.2 | 0.053543 | 0.1717 | 0.34006 | 1e-09 | 0.56 | 3 | 220 | overhead
4 | 6 | 9.4179 | Merlin | 2 | 12 | 170.2 | 0.053543 | 0.1717 | 0.34006 | 1e-09 | 0.56 | 3 | 220 | overhead
4 | 7 | 33.8304 | Merlin | 2 | 12 | 170.2 | 0.053543 | 0.1717 | 0.34006 | 1e-09 | 0.56 | 3 | 220 | overhead
6 | 5 | 4.3577 | Peacock | 2 | 12 | 306.1 | 0.062006 | 0.09547 | 0.33084 | 1e-09 | 0.83 | 3 | 220 | overhead
6 | 7 | 28.9062 | Merlin | 2 | 12 | 170.2 | 0.053543 | 0.1717 | 0.34006 | 1e-09 | 0.56 | 3 | 220 | overhead
7 | 8 | 16.7702 | Merlin | 2 | 12 | 170.2 | 0.053543 | 0.1717 | 0.34006 | 1e-09 | 0.56 | 3 | 220 | overhead
7 | 8 | 16.0636 | Merlin | 2 | 12 | 170.2 | 0.053543 | 0.1717 | 0.34006 | 1e-09 | 0.56 | 3 | 220 | overhead
7 | 9 | 15.1772 | Merlin | 2 | 12 | 170.2 | 0.053543 | 0.1717 | 0.34006 | 1e-09 | 0.56 | 3 | 220 | overhead
7 | 9 | 14.9541 | Merlin | 2 | 12 | 170.2 | 0.053543 | 0.1717 | 0.34006 | 1e-09 | 0.56 | 3 | 220 | overhead
10 | 11 | 30.2764 | Peacock | 2 | 8.5 | 306.1 | 0.062006 | 0.09547 | 0.30917 | 1e-09 | 0.83 | 3 | 132 | overhead
11 | 12 | 52.942 | Biggest | N/A | N/A | 500 | N/A | 0.053 | 0.11932 | 1.7e-09 | 0.545 | 1 | 132 | underwater
12 | 13 | 8.2014 | Merlin | 2 | 8.5 | 170.2 | 0.053543 | 0.1717 | 0.31839 | 1e-09 | 0.56 | 3 | 132 | overhead
13 | 15 | 35.5456 | Merlin | 2 | 8.5 | 170.2 | 0.053543 | 0.1717 | 0.31839 | 1e-09 | 0.56 | 3 | 132 | overhead
13 | 14 | 21.1322 | Merlin | 2 | 8.5 | 170.2 | 0.053543 | 0.1717 | 0.31839 | 1e-09 | 0.56 | 3 | 132 | overhead
14 | 15 | 15.4394 | Merlin | 2 | 8.5 | 170.2 | 0.053543 | 0.1717 | 0.31839 | 1e-09 | 0.56 | 3 | 132 | overhead
15 | 16 | 4.7127 | Merlin | 2 | 8.5 | 170.2 | 0.053543 | 0.1717 | 0.31839 | 1e-09 | 0.56 | 3 | 132 | overhead
use this to switch between cable types
cable used: |  | Cable type | Area | Resistance at 25 | Inductance | Capacitance | max_i_ka
page 4, Condor from :https://www.elandcables.com/media/38193/acsr-astm-b-aluminium-conductor-steel-reinforced.pdf | OVERHEAD | Peacock | 306.1 | 0.09547 | N/A | 1e-09 | 0.83
|  | Merlin | 170.2 | 0.1717 | N/A | 1e-09 | 0.56
page 8, Table 48, :https://new.abb.com/docs/default-source/ewea-doc/xlpe-submarine-cable-systems-2gm5007.pdf | MARINE |  | 500 | N/A | 0.38 | 1.7e-09 | 0.545
Note: capacitance for overheads is assumed, just use that for all of them, he is not even asking for it in the tables
note: for marine cable we used a 150kv cable rather than 132 for safety

## buses
bus_id2 | bus_id | name | vn_kv | geodata
0 | 0 | Ibiza (+ Formentura) | 132 | (1.430833, 38.91917)
1l | 1 | Santa Ponsa (132) | 132 | (2.506454, 39.53525)
1h | 2 | Santa Ponsa (220) | 220 | (2.507937, 39.53662)
2 | 3 | Valldurgent | 220 | (2.549167, 39.58417)
3 | 4 | Son Reus | 220 | (2.678889, 39.65083)
4h | 5 | Portol (Cas Tresorer) (220) | 220 | (2.724617, 39.56686)
4l | 5.1 | Portol (Cas Tresorer) (66) | 66 | (2.724617, 39.56686)
5 | 6 | Son Orlandis | 220 | (2.744444, 39.60028)
6 | 7 | Llubi | 220 | (3.039444, 39.67333)
7 | 8 | Murterar | 220 | (3.0925, 39.80944)
8h | 9 | Es Bessons (220) | 220 | (3.158056, 39.58194)
8l | 10 | Es Bessons (132) | 132 | (3.159638, 39.58209)
9 | 11 | Cala Mesquida | 132 | (3.427024, 39.73827)
10 | 12 | Cala en Bosch | 132 | (3.834227, 39.93175)
11 | 13 | Cuitadella | 132 | (3.855278, 40.00333)
12 | 14 | Es Mercadal | 132 | (4.095556, 39.97694)
13 | 15 | Dragonera | 132 | (4.236667, 39.89111)
14 | 16 | Mao | 132 | (4.258155, 39.89706)

## loads
location | bus_id2 | bus_id | name | vn_kv | population | demand_share | summer_p_mw | summer_q_mvar | summer_s | winter_p_mw | winter_q_mvar | winter_s
Ibiza | 0 | 0 | Ibiza (+ Formentura) | 132 | 160000 | 0.13464 | 175.4296 | 84.9644 | 194.9218 | 128.7112 | 62.3377 | 143.0124
Majorca | 1l | 1 | Santa Ponsa (132) | 132 | 103111.1111 | 0.086765 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 2 | 3 | Valldurgent | 220 | 103111.1111 | 0.086765 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 3 | 4 | Son Reus | 220 | 103111.1111 | 0.086765 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 4l | 5.1 | Portol (Cas Tresorer) (66) | 66 | 103111.1111 | 0.086765 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 5 | 6 | Son Orlandis | 220 | 103111.1111 | 0.086765 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 6 | 7 | Llubi | 220 | 103111.1111 | 0.086765 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 7 | 8 | Murterar | 220 | 103111.1111 | 0.086765 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 8l | 10 | Es Bessons (132) | 132 | 103111.1111 | 0.086765 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 9 | 11 | Cala Mesquida | 132 | 103111.1111 | 0.086765 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 10 | 12 | Cala en Bosch | 132 | 7000 | 0.0058903 | 7.675 | 3.7172 | 8.5278 | 5.6311 | 2.7273 | 6.2568
Minorca | 11 | 13 | Cuitadella | 132 | 29840 | 0.025109 | 32.7176 | 15.8459 | 36.3529 | 24.0046 | 11.626 | 26.6718
Minorca | 12 | 14 | Es Mercadal | 132 | 20285 | 0.017069 | 22.2412 | 10.7719 | 24.7124 | 16.3182 | 7.9032 | 18.1313
Minorca | 13 | 15 | Dragonera | 132 | 14232 | 0.011976 | 15.6045 | 7.5576 | 17.3383 | 11.4489 | 5.5449 | 12.721
Minorca | 14 | 16 | Mao | 132 | 29040 | 0.024436 | 31.8405 | 15.421 | 35.3783 | 23.3611 | 11.3143 | 25.9568
[7 empty] | 1303 | 631.0717 | 1447.7778 | 956 | 463.0119 | 1062.2222

## gen
island | name | coords | x_coord | y_coord | type | voltage | nearest_bus | dist_to_bus_m | notes_on_nearest_bus | capacity_mw | Gen Pot. Fraction | gen_at_peak_demand_summer | gen_at_peak_demand_winter
Ibiza | Elvissa | (38.919167, 1.430833) | 1.4308 | 38.9192 | Nat gas/diesel |  | 0 | 0.42923 |  | 292 |  | 218.7 | 134.8
Ibiza 2 | Saint Francesco | (38.691944, 1.463611) | 1.4636 | 38.6919 | Nat gas |  | 0 | 32663.6521 | Connects by sea link | 14 |  | 12 | 7.8
Mallorca | Son Reus | (39.648611, 2.680000) | 2.68 | 39.6486 | Gas | 220 | 4 | 343.8324 |  | 432.8 | 0.31809 | 303.0173 | 234.9449
Mallorca | Cas Tresorer | (39.567500, 2.689444) | 2.6894 | 39.5675 | Gas | 220 | 5 | 3916.531 |  | 400 | 0.29399 | 280.0529 | 217.1395
Mallorca | Murterar | (39.809722, 3.091944) | 3.0919 | 39.8097 | Coal/oil | 220 | 8 | 74.1676 |  | 527.8 | 0.38792 | 369.5298 | 286.5156
Menorca | Mahon (Mao) | (39.896944, 4.258611) | 4.2586 | 39.8969 | Oil | 132 | 16 |  |  | 245 |  | 113.2 | 64.6
[10 empty] | 1911.6 |  | 1296.5 | 945.8